1.0 General

1.1 - Air filter shall be cleanable, all-metal, impingement panel type. The filter shall consist of an all-metal enclosing frame and alternate layers of flat and herringbone-crimp screen media.

1.2 - Sizes shall be as noted on the enclosed drawings or other supporting materials. Such materials shall also define whether filters are to be oiled or not oiled.

2.0 Construction

2.1 - Filter media shall be multiple layers of flat and herringbone-crimped screen. There shall be at least four screen layers per media pack inch. The media pack shall be permanently fastened to the enclosing frame to maintain filter pack rigidity.

2.2 - The enclosing frame shall be manufactured of 16-gauge galvanized steel. Frame corners shall be flush, mitered, and reinforced for rigidity.

2.3 - Reinforcing rods of 1/8” steel shall assist in maintaining a rigid and durable filter pack.

2.4 - The filter shall be permanently identified as to the top of the filter for installation guidance.

3.0 Performance

3.1 - When installed vertically, the filter shall be 98% efficient on 20-micron size contaminant when operating at a velocity of 500 fpm face velocity. Initial resistance to airflow shall not exceed 0.12” w.g. at 3.6 cfm per square inch of filter face area.

3.2 - Manufacturer shall provide evidence of facility certification to ISO 9001:2008.

Filter shall be Camfil Type 44 Filter or equal.